SPECIFIER NOTE:

This specification is provided by Mid-Atlantic Coatings, Inc. as a service and is intended to be used as a guideline for preparing a project specific specification section.  Every heading may not be needed.  Delete headings not used and renumber remaining used headings to be numerically correct.

PART 1  GENERAL

1.01	SUMMARY

A.	Section Includes:

1.	Work under this section consists of surface preparation, priming, painting, and finishing work necessary to complete Work indicated or reasonably implied on Drawings.

2.	Use high performance coating systems specified in this section to finish water tank components, unless otherwise indicated.  Without restricting volume or generality, work to be performed under this section may include, but is not limited to:

a.	Exterior Steel

b.	Interior Steel Wet

c.	Interior Steel Dry

3.	Painting or finishing is not needed for following:

a.	Surfaces or materials specifically scheduled or shown on Drawings to remain unfinished

b.	Items provided with factory finish

c.	Equipment nameplates, fire rating labels, and operating parts of equipment

4.	Materials and products having factory-applied primer shall not be considered factory finished.

SPECIFIER NOTE:

Edit listings below as necessary to reflect project requirements.  List  statements drawing reader's attention to other specification sections dealing with work directly related to this section.  Listing should be limited to other sections with specific requirements pertaining to this work.

- Related Sections:

- Section 05 12 00  Structural Steel

- Section 09 60 00  High Performance Coatings

1.02	REFERENCES

SPECIFIER NOTE:

List standards referenced in the section, complete with designations and titles.  Standards and associations or industry standards should be identified here and referenced in other articles of this section by their acronym and alphanumeric designation only.  This article does not require compliance with standards, but is merely a listing of those used.

A.	Publications listed herein are part of this specification to extent referenced

B.	American Society for Testing and Materials:

1.	ASTM B 117  	Salt Spray (fog)

2.	ASTM D 16 	Terminology Relating to Paint, Varnish, Lacquer, and

Related Products

3.	ASTM D 522  	Flexibility (Method A, Conical Mandrel)

4.	ASTM D 870 	Immersion

5.	ASTM D 1014 	Exterior Exposure

6.	ASTM D 1653 	Moisture Vapor Transmission

7.	ASTM D 2794 	Impact

8.	ASTM D 3359 	Adhesion (Method B, 5 mm Crosshatch)

9.	ASTM D 3363 	Hardness

10.	ASTM D 4060 	Abrasion

11.	ASTM D 4141 	Exterior Exposure  Method C (EMMAQUA)

12.	ASTM D 4541 	Adhesion  (Method B, Type II)

13.	ASTM D 4541	Adhesion  (Method E, Type V)

14.	ASTM D 4585 	Humidity

15.	ASTM D 4587	QUV (UVA-340 Bulbs, Cycle 4:8 hours, UV/4 hours

Condensation)

16.	ASTM D 5031 	Weatherometer Exposure

17. 	ASTM G 85 	Prohesion (Annex A5)

C.	National Fire Protection Association:

1.	NFPA 101  Life Safety Code.

D.	Steel Structures Painting Council:

1.	SSPC SP-1  Specification for Solvent Cleaning

2.	SSPC SP-2  Specification for Hand Tool Cleaning

3.	SSPC SP-3  Specification for Power Tool Cleaning

4.	SSPC SP-6  Specification for Commercial Blast Cleaning

5.	SSPC SP-10  Specification for Near White Metal Blast Cleaning

6.	SSPC SP-11  Specification for Power Tool Cleaning to Bare Metal

7.	SSPC PA-1  Painting Application Specification

1.03	DEFINITIONS

A.	Terms Paint or Painting shall in a general sense have reference to sealers, primers, oil, alkyd, latex, polyurethane, epoxy, and enamel type coatings and application of these materials.

B.	Dry Film Thickness (DFT):  Thickness, measured in mils, of a coat of paint in cured state

C.	Conform to ASTM D16 for interpretation of terms used in this section.

1.04	SUBMITTALS

A.	Product Data:

1.	Submit manufacturer's literature describing products to be provided, giving manufacturer's name, product name, and product line number for each material.

2.	Submit technical data sheets for each coating, giving descriptive data, curing times, mixing, thinning, and application requirements.

a.	Provide material analysis, including vehicle type and percentage by weight and by volume of vehicle, resin and pigment.

3.	Submit manufacturer's Material Safety Data Sheets (MSDS) and other safety requirements.

B.	Shop Drawings:

1.	Submit a complete list of products proposed for use, including identifying product names and catalog numbers.

a.	Arrange in same format as Schedule of Paint Finishes below.

b.	Include applicable manufacturer's data and recommendations.

C.	Samples:

1.	Selection Samples:

a.	Submit color charts displaying manufacturer's full range of standard colors for initial selection by Engineer.

2.	Verification Samples:

a.	Submit 3 samples of each coating and color selected, showing bare, prepared surface and each successive coat.

b.	Samples shall be submitted on hardboard or metal as appropriate to coating system.  Label samples on back, identifying manufacturer, product name, and color number.

c.	Sample Size:  Not less than 12" x 12" (300 mm x 300 mm

D.	Quality Assurance Submittals:

1.	Test Reports:

a.	Provide certified test reports, prepared by an independent testing laboratory, confirming compliance with specified performance criteria.

2.	Certificates:

a.	Coatings manufacturer shall certify that coating materials utilized are "non-lead" (less than 0.06% lead by weight in dried film) as defined in Part 1303 of Consumer Product Safety Act.

b.	Provide certification that specialized equipment as may be required by manufacturer for proper application of coating materials shall be utilized for work of this Section.

c.	Provide manufacturer's certification that products to be used comply with specified requirements and are suitable for intended application.

d	Submit listing of not less than 5 of applicator's most recent applications representing similar scope and complexity to Project requirements.  List shall include information as follows:

i)	Project name and address

ii)	Name of owner

iii)	Name of contractor

iv)	Name of engineer

v)	Date of completion

3.	Manufacturer's Instructions:

a.	Submit manufacturer's installation procedures which shall be basis for accepting or rejecting actual installation procedures.

4.	Exterior Water Tank Containment:

a.	Submit the containment designs and plans for use on the tank exterior and manufacturer's installation procedures which shall be basis for accepting or rejecting actual installation procedures.

1.05	QUALITY ASSURANCE

A.	Qualifications:

1.	Provide products from a company specializing in manufacture of high performance coatings with a minimum of 10 years experience.

2.	Applicator shall be trained in application techniques and procedures of coating materials and shall demonstrate a minimum of 2 years successful experience in such application.

a.	Maintain, throughout duration of application, a crew of painters who are fully qualified to satisfy specified qualifications.

3.	Single Source Responsibility:

a.	Materials shall be products of a single manufacturer or items standard with manufacturer of specified coating materials.

b.	Provide secondary materials which are produced or are specifically recommended by coating system manufacturer to ensure compatibility of system.

B.	Regulatory Requirements:

1.	Conform to applicable codes and ordinances for flame, fuel, smoke, and volatile organic compound (VOC) ratings requirements for finishes at time of application.

C.	Pre-Installation Meetings:

1.	Schedule a conference and inspection to be held on-site before field application of coating systems begins.

2.	Conference shall be attended by Contractor, Owner's representative, Engineer, coating applicators, and a representative of coating material manufacturer.

3.	Topics to be discussed at meeting shall include:

a.	A review of Contract Documents and accepted shop drawings shall be made and deviations or differences shall be resolved.

b.	Review items such as environmental conditions, surface conditions, surface preparation, application procedures, and protection following application.

c.	Establish which areas on-site will be available for use as storage areas and working area

4.	Pre-construction conference and inspection shall serve to clarify Contract

Documents, application requirements and what work should be completed

before coating application can begin.

5.	Prepare and submit, to parties in attendance, a written report of pre-installation conference.Report shall be submitted with 3 days following conference.

D.	Field Samples:

1.	Provide a full coating system to the required sheen, color, texture, and recommended 	coverage rates. Simulate finished lighting conditions for reviewing in-place work

2.	The Architect or Owners Representative will select one room, area, or combination of areas and surfaces and conditions for each type of coating and substrate to be coated. Apply 	coatings in this room, area, combination of areas

and surfaces according to the schedule, or as specified. After finishes are accepted, this room, area or combination of areas and surfaces will serve as the standard of quality and for evaluation of coating systems of similar nature.

3.	A manufacturer’s representative shall be available upon request by the General Contractor or Painting subcontractor, to advise applicator on proper application technique and procedures.

E.	Tank Containment:

1.	Provide designs and plans for providing full contaminat around the exterior of water tank. Designs and plans shall be submitted with the bid for approval by a structural engineer.

2.	Containment shall fully contain any air borne grit from field sandblasting and overspray or drips from the field painting operations.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Packing, Shipping, Handling, and Unloading:

1.	Deliver products in manufacturer's original unopened containers. Each container shall have manufacturer's label, intact and legible.  Containers shall fully identify brand, type, grade, class, and other qualifying information used to describe contents.

2.	Include on label for each container:

a.	Manufacturer's name

b.	Type of paint

c.	Manufacturer's stock number

d.	Color name and number

- Instructions for thinning, where applicable

B.	Storage and Protection:

1.	Store materials in a protected area, away from construction activities.  Restrict storage area to paint materials and related equipment.

2.	Maintain temperature in area of storage between 40 degrees F (4 degrees C) and 110 degrees F (43 degrees C).

3.	Comply with health and fire safety regulations.

4.	Remove damaged materials from Site.

1.07	PROJECT CONDITIONS

A.	Environmental Requirements:

1.	Apply coating materials under conditions as follows:

a.	Air temperature shall not be below 35 degrees F (2 degrees C) or above 110 degrees F (43 degrees C).

b.	Refer to specific product information sheets for minimum surface temperature requirements.  Surface temperatures shall be at least 5 degrees F (15 degrees C) above dew point and in a rising mode.

c.	Relative humidity shall be no higher than 85%.

d.	For exterior spray application, wind velocity shall be less than 15 mph (25 kph).

e.	Atmosphere shall be relatively free of airborne dust.

1.08	SEQUENCING

A.	Coordination:

1.	Perform work in proper sequence with work of other trades to avoid damage to finished work.

2.	Where coatings are scheduled to be applied over shop applied coatings, coordinate work of such shop applied products to ensure compatibility with field applied coating systems.

1.09		CONTRACTOR PRE-QUALIFICATION

- All contractors bidding this project shall provide documentation of having repainted

five (5) potable water storage tanks within 12 months of the bid date.

PART 2  PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.	To define requirements for materials, size, and design, this specification lists specific products manufactured by Tnemec Company,  Inc. of Kansas City, Missouri  Materials specified herein are cited as minimum standard of quality which will be acceptable.

B.	Materials specified herein shall not preclude consideration of equivalent or superior materials.  Suggested equivalent materials or other substitutions shall be submitted to Engineer for consideration in compliance with substitution procedures in Section 01600 of this Project Manual.

1.	Requests for substitution shall include evidence of satisfactory past performance on Correctional Facilities.

2.	Substitutions will not be considered that change number of coats or do not meet specified total dry film thickness.

2.02	STEEL COATING MATERIALS

SPECIFIER NOTE:

Delete materials not applicable to project.  For alternate materials and systems contact

your Tnemec Representative or Tnemec Technical Services.

A.	Tnemec - Series V69 and V69F Hi-Build Epoxoline II

1.	Generic Type:  Polyamidoamine Epoxy

2.	Finish: Satin

3.	Properties:

a.	Solids by Volume:  67 +/- 2.0% (mixed)

b.	VOC: Unthinned: 2.38 lbs/gallon (285 grams/litre)

4. 	Performance Criteria:

a.	Abrasion: ASTM D4060, (CS-17 Wheel, 1,000 grams load). No more than 140 mg. loss after 1,000 cycles

b. 	Adhesion: ASTM D 4541Type II Fixed Alignment Adhesion Tester. No less than 1,583 psi (10.91 MPa) pull, average of three tests.

c. 	Adhesion: ASTM D4541 Type V Self-Aligning Adhesion Tester. No less than 1,943 psi (13.40 MPa) pull; average of three tests.

d.	Exterior Exposure: ASTM D 1014. No blistering, cracking, checking, rusting or delamination of film.  No more rust creepage at scribe after (5) years exposure

e.	Exterior Exposure: Exposed at 45 degrees facing south (light industrial area). No blistering, cracking or delamination of film.  No rust creepage at scribe or no rusting at edges after 72 months exposure.

f.	Fresh Water: Continuous immersion in tap water at 750F (240C). No blistering, cracking, rusting or delamination of film after four years

g.	Humidity: ASTM D4585. No blistering, cracking, rusting or delamination of film after 4,500 hours exposure

h.	Immersion: ASTM D 870. No blistering, cracking, checking, rusting or delamination of film after two years or 17,088 hours continuous water immersion.

i.	Moisture Vapor Transmission: ASTM D 1653. No more than 9.9 g/m2 24 hours water vapor transmission and no more than 0.31 grains/ft2 hour in Hg. Water vapor permeability

j.	Prohesion: ASTM G 85. No blistering, cracking, checking, rusting or delamination of film. No rust creepage at scribe after 5,000 hours exposure.

k.	Salt Spray (Fog). ASTM B117. No blistering, cracking or delamination of film.  No more than 1% rusting on plane. No more than 1/64” rust creepage at scribe after 10,000 hours  exposure and no more than 1/16” rust creepage at scribe after 6,700 hours exposure.

B.	Tnemec – Series H0 90-97 Tneme-Zinc (Ferrous Metal Shop/Field Primer)

1.	Generic Type:  Aromatic Urethane, Zinc-Rich Primer

2.	Description:  Two-component, moisture-cured, zinc-rich primer

3.	Properties:

a.	Solids by Volume:  63.0 +/- 2.0% (mixed)

b.	VOC: 2.67 lbs/gallon (320 grams/litre)

c.	HAPS:

i)	Series 90-97 – 4.24 lbs/gal solids

ii)	Series HO90-97 – 1.9 lbs/gal solids

4.	Performance Criteria:

a.	Adhesion: ASTM D 4541 (TTM-34) Type II Fixed Alignment Adhesion Tester. No less than 1,516 psi (10.46 MPa) adhesion, average of three tests.

- Adhesion: ASTM D4541 (TTM-34) Type V Self-Aligning Adhesion Tester. No less than 2,083 psi (6.89 MPa) pull.

- Exterior Exposure: ASTM D 1014 – Kansas City 450 facing South. No blistering, cracking, rusting or delamination of film. No more than 1/64” rust creepage at scribe after 5 years light industrial exposure.

- Galvanic Protection: One coat aromatic urethane, zinc-rich coated steel panel containing several holidays is placed in a container of tap water. The panel’s potential is measured by a voltmeter with the positive (+) pole attached to a bare spot on the panel above the water line and the negative (-) pole attached to an Ag/AgC1 referenced electrode immersed in the tap water.True theorectical galvanic action of the zinc having actual zinc-to-zinc contact would show a potential of 1100 millivolts. A range of 1100 millivolts to 750 millivolts would indicate galvanic action is occuring. The optimum potential is 850 millivolts. A potential of 500 millivolts or less would indicate that the coating is only acting as a barrier coating. The average measured potential of 90-97 is 878 millivolts.

- Humidity: ASTM D 4585. No blistering, cracking, rusting or delamination of film after 4,000 hours exposure.

f. 	Salt Spray (Fog). ASTM B 117. No blistering, cracking, or delamination of film. No more than 1% rusting on plane and no more than ¼” rust creepage at scribe after 20,000 hours exposure. No more than 1/32”  rust creepage at scribe after 10,000 hours exposure.

g.	Prohesion: ASTM G 85 Prohesion Cabinet Testing.No blistering, cracking, rusting or delamination of film. No more than 1/64” creepage at scribe after 15,000 hours.

h.	Static Fatigue (Slip Coefficient & Tension Creep). Meets the requirements of a Class B surface with a mean slip coefficient no less than 0.50 and a tension creep not in excess of .005 inch (.13 mm)

C.	Tnemec - Series 94-H2O - Hydro-Zinc

1.	Generic Type:  Aromatic Urethane, Zinc-Rich

2.	Description:  Two-component, moisture cured zinc-rich primer for interior and exterior of steel potable water storage facilities.

3.	Properties:

a.	Solids by Volume:  62.0 +/- 2.0% (mixed)

b.	VOC: 0.80 lbs/gallon (96grams/litre)

c.	HAPS: 0.8 lbs/gal solids.

3.	Performance Criteria:

a.	Adhesion: ASTM D 4541 (TTM-34) Type II Fixed Alignment Adhesion Tester. No less than 1,533 psi adhesion.

b.	Adhesion: ASTM D4541 (TTM-34) Type V Self-Aligning Adhesion Tester. No less than 1,730 psi adhesion.

c. 	Cathodic Disbondment: ASTM G 8, Method A. No rusting, blistering, cracking or delamination and no undercutting at holiday after 30 day exposure.

d.	Galvanic Protection: A one coat aromatic urethane zinc-rich coated steel panel containing several holidays is placed in a container of tap water. The panel’s potential is measured by a voltmeter with the positive (+) pole attached to a bare spot on the panel above the water line and the negative (-) pole attached to an Ag/AgC1 referenced electrode immersed in the tap water. True theorectical galvanic action of the zinc having actual zinc-to-zinc contact would show a potential of -1100 millivolts. A range of -1100 millivolts to -750 millivolts would indicate galvanic action is occuring. The potential of -654 millivolts or less would indicate that the coating is only acting as a barrier coat when tested with a Ag/AgCl reference electrode. The average measured potential of 94-H20 is 818 millivolts.

- Immersion: ASTM D 870. No blistering, cracking, rusting or delamination of film after two years immersion.

- Prohesion: ASTM G 85 Prohesion Cabinet Testing. No blistering, cracking, rusting or delamination of film. No more than 1/8” creepage at scribe after 10,000 hours.

- Re-coat Time/Immersion: Series 94-H2O steel panles were exposed to direct sunlight for one, two, six and months. One set of panels was topcoated (without scarification) with a two-component epoxy and another set with an acrylic polyurethane. All panels were then exposed to 10 freeze/thaw cycles and adesion rated in accordance with ASTM D 3359, Method B (crosshatch). No rusting, blistering, delamination, or other film defects after 12 months immersion.

j.  	Salt Spray (Fog): ASTM B117. No blistering, cracking or delamination of film. No more than 1% rusting on plane and no more than 1/16”rust creepage at scribe after 10,000 hours exposure.

D.	Tnemec - Series V140 or V140 F Pota-Pox Plus (Potable Water Coating)

1.	Generic Type:  Polyamidoamine Epoxy

2.	Properties:

a.	Solids by Volume:  67 +/- 2.0% (mixed)

b.	VOC: Unthinned: 1.95 lbs/gallon (234 grams/litre)

3.	Performance Criteria:

a.	Abrasion: ASTM D 4060 (CS-17 Wheel, 1,000 grams load). No more than 140 mg. loss after 1,000 cycles

b.	Adhesion:  ASTM D 4541 Type II Fixed Alignment Adhesion Tester. No less than 1,583 psi (10.91 MPa) pull, average of three tests.

c.	Adhesion: ASTM D 4541 Type V Self-Aligning Adhesion Tester. No less than 1,943 psi (13.40 MPa) pull; average of three tests.

d.	Exterior Exposure. ASTM D 1014. No blistering, cracking, checking, rusting or delamination of film. No rust creepage at scribe after (5) years exposure. To evaluate Polyamidoamine Epoxy when exterior exposed at 45 degrees south.

e. 	Humidity: ASTM D 4585. No blistering, cracking, delamination of film after 10,000 hours exposure.

f. 	Immersion (fresh water). ASTM D 870. No blistering, cracking, checking, rusting or delamination of film after two years continuous water immersion.

g.  	Moisture Vapor Transmission: ASTM D 1653. No more than 9.9 g/m2 24 hours water vapor transmission and no more than 0.31 grains/ft2 hour in Hg. Water vapor permeability.

h.	Prohesion: ASTM G 85. No blistering, cracking, checking, rusting or delamination of film. No rust creepage at scribe after 5,000 hours exposure.

i.  	Salt Spray (Fog). ASTM B117. No blistering, cracking or delamination of film. No more than 1% rusting on plane. No more than 1/64” rust creepage at scribe after 10,000 hours exposure. No more than 1/16” rust creepage at scribe after 6,700 hours exposure.

E.	Tnemec – Series 700V & 701V Hydro Flon

1.	Generic Type:  Fluropolmer Polyurethane Exterior Finish Coat

2.	Properties:

- Solids by Volume:

- Series 700V: 51.0 +/- 2.0%

- Series 701V: 56.0 +/- 2.0%

- VOC:

- Series 700V: 0.83 lbs/gallon (98 grams/litre)

- Series 701V: 0.81 lbs/gallon (97 grams/litre

- Gloss Levels:

- Series 700V: Gloss

- Series 701V: Semi-Gloss

- Performance Criteria

a.	Abrasion: ASTM D4060, (CS-17 Wheel, 1,000 grams load). No more than 103 mg loss after 1,000 cycles.

b.	Adhesion: ASTM D 4541 (Method B, Type II Tester). No less than 1,333 psi (9.19 MPa) pull, average of three tests.

c.	Adhesion: ASTM D 4541 (Method E, Type V Tester). No less than 1,930 psi (13.3 MPa) pull, average of three tests.

d. 	Exterior Exposure: Exposed at 45 degrees facing south. No blistering, cracking, rusting or delamination of film. No less  than 87% gloss retention (8.9 units gloss change) and 2.99 DED FMCII (MacAdam units) color change after 24 months.

e.	Exterior Exposure: ASTM D 4141, Method C (EMMAQUA). No blistering, cracking or chalking. No less than 96% gloss retention (3.2 units gloss change) and 0.18 DED Hunter Lab color change after 1,260 M/J m2 EMMAQUA exposure, average of five tests in five colors.

f.	Flexibility: ASTM D 522 (Method A – Conical Mandrel). No less than 14.83% elongation average of three tests

g.	Graffiti Resistance: The following graffiti materials applied to coating and allowed to 7 days. Reagent:

Series 680 		Xylene		MEK

Acrylic Spray Paint	Removal		Removal	Removal

Epoxy Spray Paint	Removal		Removal	Removal

Markette Marker	Removal		Removal		Removal

Ball Point Ink		Removal		Removal		Removal

Crayon			Removal			Removal		Removal

Lipstick			Removal			Removal		Removal

Some slight gloss loss and/or softening may occur depending on the amount

of effort required for removal of the graffiti and length of exposure of the

underlying coating to the cleaning solvents.

h.	Hardness: ASTM D3363. No gouging or scratching with an 8H or less pencil.

i. 	Humidity: ASTM D 4585. No blistering, cracking, rusting or delamination of film after 3,000 hours exposure.

j.	Impact: ASTM D 2794. No visible cracking or delamination of film after 34.6 inch/pounds (3.9J) or less direct impact

k. 	QUV: ASTM D 4587 (UVA-340 Bulbs, Cycle 4:8 hours UV/4 hours condensation). No blistering, cracking, or chalking. No less than 93% gloss retention (5.7 units gloss change) and 2.21 DED FMCII ( MacAdam Units) color change after 10,000 hours exposure, average of five tests in five colors. No blistering, cracking, or chalking. No less than 60% gloss retention (31.4 units gloss change) and 1.89 DED FMCII (MacAdam Units) color change after 25,000 hours exposure, average of five tests in five colors.

l.. 	Salt Spray (Fog): ASTM B 117. No blistering, cracking, rusting or delamination of film. No more than 1/32 inch rust creepage at scribe after 10,000 hours exposure. No blistering, cracking, rusting or delamination of film. No more than 1/8 inch rust creepage at scribe after 10,000 hours exposure. No blistering, cracking, rusting or delamination of film. No more than 1/16 inch rust creepage at scribe after 10,000 hours exposure.

m.	Weatherometer Exposure: ASTM D 5031. No blistering, cracking, or

chalking. No less than 92% gloss retention (6 units gloss change) and 0.73

DED Hunter Lab Scale color change after 5,000 hours exposure.

E.	Tnemec – Series 740 & 750 Endura-Shield

1.	Generic Type: Low VOC Hybird Aliphatic Polyurethane

2.	Gloss level: Series 740 (gloss) Series 750 (semi-gloss)

3.	Properties:

a.	Solids by Volume:

i)	Series 740: 74 +/- 2.0% (mixed)

ii)	Series 750: 72 +/- 2.0% (mixed)

b.	VOC:

i)	Series 740: 0.77 lbs/gallon (92 grams/litre)

ii)	Series 740: 0.82 lbs/gallon (99 grams/litre)

4.	Performance Criteria:  Unless otherwise indicated, coating systems for tests were applied to SSPC SP10 cleaned steel and cured at 750F (240C)

a.	Abrasion: ASTM D4060, (CS-17 Wheel, 1,000 grams load. No less than 116 mg loss after 1,000 cycles.

b.	Adhesion: ASTM D3359, (Method B, 5 mm Crosshatch). No less than a rating of 5

c.	Adhesion: ASTM D4541 (Method B, Type II). No less than 1,525 psi (10.51 MPa) pull; average of three tests.

d.	Adhesion: ASTM D4541 (Method E, Type V): No less than 1,860 psi (12.82 MPa) pull; average of three tests.

e.	Exterior Exposure: ASTM D 4141 Method C (EMMAQUA). No blistering, cracking or chalking. No less than 97% gloss retention (2 units gloss change) and 0.11 DED Hunter lab scale color change after 500 MJ exposure.

f.	Flexibility: ASTM D522 (Method A, Conical Mandrel). No less than 12.6% elongation, average of three tests.

g. 	Flexibility: ASTM D522 (Method B, Cylindrical Mandrel). No cracking or delamination of film when tested with ¼” mandrel. No less than 18.7% elongation, average of three tests.

h.	Graffiti Resistance: The following graffiti materials applied to coating and allowed to dry for seven days.

Reagent:		Series 680 	Xylene		MEK

Acrylic Spray Paint	Removal	Removal		Removal

Alkyd Spray Paint	Removal	No Effect		Diff.to remove

Epoxy Spray Paint	Removal	No Effect		Removal

Ball Point Ink		Removal	Faint Shadow	Removal

Crayon			Removal	Removal		Removal

Markette Marker	Removal	Heavy Shadow	Faint Shadow

i. 	Humidity: ASTM D4585. No blistering, cracking, rusting or delamination of film after 1,500 hours exposure

J.	Impact: ASTM D 2794. No cracking or delamination of film after 32 inch-pounds (3.6 J) diecrt impact, avaerage of three tests.

k.	Prohesion: ASTM G 85. No blistering, cracking, rusting or delamination of film. No more than 1/32 inch (0.8 mm) rust creepage at scribe after 1,500 hours exposure.

l.	QUV Exposure: ASTM D 4587 (UVA-340 bulbs, Cycle 4:8 hours UV/4

hours condensation. No blistering, cracking, chalking or delamination of

film. No less than 96%% gloss retention (3 units gloss change) and 0.42

DED FMCII (McAdam units) color change after 2000 hours exposure.

m.	Salt Spray (Fog): ASTM B117. No blistering, cracking, rusting or delamination of film. No more than 1/64 inch rust creepage at scribe after 5,000 hours exposure.

2.03	EXTERIOR CONCRETE COATING FOR COMPOSITE TANKS

- Tnemec Series 156 (smooth) 157 (sand texture) Envirocrete – Self Primer & Finish

Coat

- Generic Type:  Modified Waterborne Acrylate

- Colors: Opaque

- Properties:

- Solids by Volume:

- Series 156:  50.9 +/- 2.0%

- Series 157:  55.5 +/- 2.0%

b.	VOC:  Unthinned

i)	Series 156:  0.41  lbs/gallon (49 grams/litre)

ii)	Series 157:  0.38  lbs/gallon (45 grams/litre)

- Performance Criteria:

- Adhesion: ASTM D3359, (Method B, Crosshatch) No less than a

rating of 5 out of 5 (5 being the best adhesion).

- Freeze/Thaw: ASTM D2246. No cracking over concrete after 20

cycles.

- Fungal Resistance: ASTM D 3273 - 900F (320C); 95 - 98% relative

humidity, suspended 3" (75 mm) above soil containing aspergillus niger, aspergillus oryzae and an unknown species of penicillium. No more than slight mold growth after five weeks exposure.

- Humidity: ASTM D4585. No blistering, cracking or visible damage

after 2,000 hours exposure.

- Moisture Vapor Transmission: ASTM D1653 (Method B), Wet Cup,

Condition C at 100 degrees F (38 degrees C):

a)	Average 125 grams/meter2 in 24 hours (smooth)

b)	Average 305 grams/meter2 in 24 hours (textured)

- QUV Exposure: ASTM G53 (FS-40 lamps; four hours UV/60 degrees C, four hours CON/50 degrees C). No blistering, cracking or chalking. No more than 3.0 Mac Adam units color change after 4,000 hours exposure.

- Salt Spray (Fog): ASTM B 117. No blistering, cracking or delamination of film. No visible damage to coating or substrate after 5,000 hours.

- Tensile Strength & Elongation: ASTM D 2370. Elongation no less than 200 percent average of five tests. Tensile strength no less than 250 psi (1.7 MPa), avearge of three tests.

- Wind Driven Rain: TT-C-555B, Section 4.4.7.3. No damage to coating

or substrate. No visible moisture on the back of lightweight block after

48 hours exposure.

2.04	ANTI GAFFITI COATING FOR LOWER PORTION OF A COMPOSITE TANK

A.	 Tnemec – Series V626 Dura-Pell GS

1.	Generic Type: RTV Silicone Rubber Water Repellent & Non-Distructive Graffiti Protectant

2. 	Colors: Clear

- Properties:

a.	Solids by Volume: 15%

b.	VOC:  Unthinned: 0.81 lbs/gal (97 g/l)

- Performance Criteria:

a. 	Accelerated Weathering: ASTM C 793 - No signs of deterioration except for dirt accumulation after 4000 hours exposure.

b.	Chloride Ion Penetration: AASHTO T-259 - No less than a 1500% reduction in the chloride in the chloride ion content when compared to untreated concrete.

c.	Hydrostatic Pressure: ASTM D 751 - No less than 35 psi (241 kPa) hydrostatic pressure resistance.

d.	Moisture Vapor Transmission: ASTM E 96 - No less than 12 perms water vapor permanence.

e.	Water Penetration and Leakage: No dampness or water leakage of wall following 4 hours of continuous water exposure.

2.05	WATER REPELLENT COATING FOR UPPER PORTION OF A COMPOSITE TANK

- Chemprobe Series V662 Prime-A-Pell Plus

1.	Generic Type: Modified Siloxane/Silane with Diffused Quartz Carbide

2.	Color: Milky-white when applied, dries invisible, leaving the aesthetic appearance of the substrate unchanged.

3.	Properties:

a.	Active contents:   42% +/- 2.0% (mixed)

b.	Weight per gallon: 6.91 lb/gal (828 g/l)

c.	VOC (unthinned): 3.3 lbs/gal (395) g/l

d.	Solubility in Water: None

4.	Performance Criteria:

a.	Absorption: RILEM 11.4, 5.0 ml, 20 minutes. Applied to cast mortar cubes, Ohio sandstone and Fired clay Brick. No greater than 0.25 ml drop in the water lebvel of the tube during the 20 minutes evaluation.

b.	Depth Penetration: ASTM E514. Minimum 90% reduction in leakage rate in comparison of treated and untreated specimens.

c.	Moisture Vapor Transmission: ASTM E96. No less than 87% retention of water vapor transmission characteristics of fired clay paver. No less than 84% retention of water vapor transmission characteristics of Ohio sandstone. No less than 87% retention of water vapor transmission characteristics of cast mortar.

d.	QUV: ASTM G-53 (2500 Hours). No reduction in water repellent performance after 5,000 hours expsoure.

e.	Water Absorption: ASTM C 67. No less than 96% retention in water vapor transmission as compared to untreated samples following 24 hours of submersion. ASTM C 97. No less than 93% retention in water vapor transmission as compared to untreated samples following 24 hours of submersion. ASTM C 140. No less than 87% retention of water vapor transmission as compared to untreated samples following 24 hours of submersion

2.06	SOURCE QUALITY CONTROL

A.	Testing Laboratory Services:

1.	Documents:

a.	Review Contract Documents and applicable sections of referenced standards.

2.	Shop Painting Inspection:

a.	Verify cleaning operations to surfaces are to condition specified.

b.	Verify conformance of paint to specification.

c.	Check for thickness of each coating, final thickness and holidays.

d.	Check touchup for final finish.

3.	Reports:

a.	Submit written progress reports describing tests and inspections made and showing action taken to correct nonconforming work. Report uncorrected deviations from Contract Documents.

PART 3  EXECUTION

  - ACCEPTABLE INSTALLERS

- Submit certification letter listing (5) jobs of similar in material and extent to those

systems indicated for the project.

3.02	EXAMINATION

A.	Site Verification of Conditions:

- Examine areas and conditions under which application of coating systems shall be performed for conditions that will adversely affect execution, permanence, or quality of coating system application.

- Correct conditions detrimental to timely and proper execution of Work.

- Do not proceed until unsatisfactory conditions have been corrected.

- Commencement of installation constitutes acceptance of conditions and responsibility for satisfactory performance.

3.03	PREPARATION

A.	Protection:

1.	Take precautionary measures to prevent fire hazards and spontaneous combustion.  Remove empty containers from Site.

2.	Place cotton waste, cloths and hazardous materials in containers, and remove from Site daily.

3.	Provide drop cloths, shields, and other protective equipment.

4.	Protect elements surrounding work of this section from damage or disfiguration.

5.	As Work proceeds, promptly remove spilled, splashed, or splattered materials from surfaces.

6.	During application of coating materials, post Wet Paint signs.

7.	During application of solvent-based materials, post No Smoking signs.

B.	Shop And Field Surface Preparation :

1.	General Requirements:

a.	Prior to application of primer, surfaces shall be prepared to receive specified coating system in compliance with manufacturer's recommendations and specifications of Steel Structures Painting Council as indicated in Schedule below

b.	Clean surfaces of residual deposits of grease, scale, rust, oil, dirt, and other foreign matter, immediately prior to priming.  Surfaces to be coated shall be clean, dry, smooth and free from dust and foreign matter which will adversely affect adhesion or appearance.

2.	Ferrous Metal Surfaces:

a.	Interior Wet – SSPC-SP10 Near White Blast Cleaning

b.	Interior Dry – SSPC-SP6 Commercial Blast Cleaning

c.	Exterior - SSPC-SP6 Commercial Blast Cleaning

3. 	Concrete Surfaces:

a.	Exterior – High pressure hot water blast to remove dirt and bond breakers or other surface contaminants.

4.	All surface preparation procedures should be done in conformance with local,

state, and federal OSHA and EPA guidelines. Waste generation and removal should be in conformance with all OSHA and EPA guidelines. Lead content of existing coatings shall be determined by the owner prior to the bid date.

3.04	APPLICATION

A.	General Requirements:

1.	Apply coating systems in compliance with manufacturer's instructions and using application method best suited for obtaining full, uniform coverage of surfaces to coated.

2.	Apply primer, intermediate, and finish coats to comply with wet and dry film thickness and spreading rates for each type of material as recommended by manufacturer.

a.	Application rates in excess of those recommended and fewer numbers of coats than specified shall not be accepted.

3.	Number of coats specified shall be minimum number acceptable. Apply additional coats as needed to provide a smooth, even application.

a.	Closely adhere to re-coat times recommended by manufacturer.  Allow each coat to dry thoroughly before applying next coat. Provide adequate ventilation for tank interior to carry off solvents during drying phase.

4.	Employ only application equipment that is clean, properly adjusted, and in good working order, and of type recommended by coating manufacturer.

5.	After surface preparation, interior weld seams shall be brush applied.

6.	Make edges of paint adjoining other materials or colors sharp and clean, without overlapping.

3.05	REPAIR/RESTORATION

A.	At completion of Work, touchup and restore finishes where damaged.

B.	Defects in Finished Surfaces:

1.	When stain, dirt, or undercoats show through final coat, correct defects and cover with additional coats until coating is of uniform finish, color, appearance and coverage.

C.	Touchup of minor damage shall be acceptable where result is not visibly different from surrounding surfaces.  Where result is visibly different, either in color, sheen, or texture, recoat entire surface.

3.06	FIELD QUALITY CONTROL

A.	Testing Laboratory Services:

1.	Documents:

a.	Review Contract Documents and applicable sections of referenced standards.

2.	Field Painting Inspection:

a.	Verify cleaning operations to surfaces are to condition specified.

b.	Verify conformance of paint to specification.

c.	Check for thickness of each coating, final thickness and holidays.

d.	Check touchup for final finish.

3.	Reports:

a.	Submit written progress reports describing tests and inspections made and showing action taken to correct nonconforming work.  Report uncorrected deviations from Contract Documents.

B.	Manufacturer's Field Service:

1.	Coatings manufacturer shall be available to provide on-site inspections, technical assistance, and guidance for application of coating system as needed.

C.	Water Tank Containment:

1.	All exterior water tank containment shall be installed in accordance with the engineer approve designs and plans.

2.	No coating work shall proceed until field inspections are engaged and approved by the owners representative.

3.07	CLEANING

A.	At completion of day's work, remove from Site rubbish and accumulated materials.

B.	Clean paint spots and other soiling from pre finished surfaces and surfaces with integral finish.  Use solvents which will not damage finished surface.

C.	Leave storage area clean and in same condition indicated for equivalent spaces in Project.

3.08	PROTECTION/HANDELING

- Protect work against damage until fully cured.  Provide signs identifying wet surfaces until surfaces are adequately cured.

- Separate shop painted members using wood donage during transportation and when storing at the jobsite.

- Use nylon slings to load, unload and secure shop painted steel members.

- The contractor shall minimize damage of the coating film when loading, unloading and shipping shop painted steel members.

3.09	WASTE MANAGEMENT

A.	General Requirements:

1.	Place materials defined as hazardous or toxic waste in designated containers.

2.	Return solvent and oil soaked rags for contaminant recovery and laundering or for proper disposal.

3.	Do not dispose of paints or solvents by pouring on ground.  Place in designated containers for proper disposal.

4.	Where paint recycling is available, collect waste paint by type and provide for delivery to recycling or collection facility.

B.	Containment/Disposal Requirements:

1.	Surface Preparation Debris Containment:

a.	When required by federal, state or local regulation, entire tank and structure shall be enclosed and surface preparation debris contained.

b.	Refer to SSPC 61 Guide for Containing Debris Generated During Paint Removal Operations.

2.	Disposal of Surface Preparation Debris:

a.	Refer to SSPC 71 Guide for the Disposal of Lead-Contaminated Surface Preparation Debris.

b.	Surface preparation debris shall be disposed of in compliance with applicable federal, state and local regulations.

3.	Containment/Disposal Costs:

a.	Painter shall be responsible for costs associated with containment and waste disposal that may result from execution of this Project.

3.10	SCHEDULE OF COATING SYSTEMS

*All coating thickness are expressed in dry film thickness (DFT.)

SPECIFIER NOTE:

Delete coating scheduleles that are not applicable to project. For alternate systems contact

your Tnemec Representative or Tnemec Technical Services.

A.	Steel Exterior - Shop primer, and Field Applied System

1.	Surface Preparation:  SSPC SP6 Commercial Blast Cleaning

2.	Primer/Shop or Field Coat: Tnemec Series H90-97 Tneme-Zinc

a.	Dry Film Thickness:  2.5 to 3.5 mils

3.	Stripe Coat:  Series Tnemec Series H90-97 Tneme-Zinc

(Shall be applied by brush to all weld seams, angles and edges)

a.	Dry Film Thickness:  2.5 at 3.5 mils DFT

4.	Tnemec Series 740 or 750 Endura-Shield

a.	Dry Film Thickness:  3.0 to 5.0 mils

5	Finish Coat: Tnemec Series 700V Hydroflon

a.	Dry Film Thickness:  2.0-3.0 mils

6.   	Total Dry Film Thickness:  7.5 to 11.5 mils

B.	Steel Interior Wet – Shop primer, and Field Applied System

1.	Surface Preparation: SSPC-SP10 Near White Blast Cleaning

2.	Shop or Field Primer: Tnemec Series 94-H20 Hydro-Zinc

a.	Dry Film Thickness:  2.5 at 3.5 mils DFT.

3.	Stripe Coat:  Series Tnemec Series 94-H20 Hydro-Zinc

(Shall be applied by brush to all weld seams, angles and edges)

a.	Dry Film Thickness:  2.5 at 3.5 mils DFT

4.	First Coat: Tnemec Series V140 or V140F Pota-Pox Plus – 1255 Beige

a.	Dry Film Thickness: 3.0 to 5.0 mils DFT.

5.	Finish Coat: Tnemec Series 141 Epoxoline - WH03 Tank White

a.	Dry Film Thickness:  10.0 to 12.0 mils DFT

6.	Total Dry Film Thickness:  15.5 to 20.5 mils

C.   	Steel Interior Dry – Field Applied System

1.	Surface Preparation:  SSPC SP6 Commercial Blast Cleaning

2.	Primer/Shop Coat:  Tnemec Series H90-97 Tneme-Zinc or 94-H20 Hydro-Flon

a.	Dry Film Thickness:  2.5 to 3.5 mils

3.	Stripe Coat:  Series Tnemec Series H90-97 Tneme-Zinc or 94-H20 Hydro-Flon

(Shall be applied by brush to all weld seams, angles and edges)

a.	Dry Film Thickness:  2.5 at 3.5 mils DFT

4.	First Coat: Tnemec Series V69-color H.B. Epoxoline II

a. 	Dry Film Thickness: 3.0 to 5.0 mils DFT

5.	Finish Coat: Tnemec Series V69-color H.B. Epoxoline II

a. 	Dry Film Thickness: 3.0 to 5.0 mils DFT

6.	Total Dry Film Thickness:  8.5 to 13.5 mils

D.	(Use when color is required) Exterior Concrete – Opaque Color Weather Proofing

Material

1.	Surface Preparation – High pressure hot water blast cleaning.

2.	First Coat: Series 156 Envirocrete

a.	Dry Film Thickness: 4.0 to 6.0 mils DFT

3.	Finish Coat: Series 156 Envirocrete

a.	Dry Film Thickness: 4.0 to 6.0 mils DFT

E.	Exterior Concrete, Water Repellent & Anti-Graffiti Coating (Apply up to 14 feet

high)

1.	Surface Preparation – High pressure hot water blast cleaning.

2.	First Coat: Series V626 Dur A Pell

a.	Coverage Rate: 200 to 300 sq ft per gallon

3.	Finish Coat: Series V626 Dur A Pell

a.	Coverage Rate: 200 to 300 sq ft per gallon

G.	(Optional Protection) Exterior Concrete, Water Repellent (Apply above 14 feet)

1.	Surface Preparation – High pressure hot water blast cleaning.

2.	One Coat: Series V662 Prime A Pell Plus

a.	Coverage Rate: 100 to 200 sq ft per gallon

3.11		FIRST ANNIVERSARY INSPECTION

A.	The Owner shall establish a time period for inspection of paint systems within

the contract guarantee period in accordance with Section 9 of AWWA D102.  The Contractor shall comply with said Section 9 at no additional cost to the Owner.

3.12			CLEANING AND DISINFECTION

- Final cleaning and bacteriological disinfecting shall be performed by one on

the methods stated in AWWA D105 such that the water sample taken after disinfecting complies with the requirements of the State Public Health Authority having jurisdiction and the tank is approved by said State Authority to be placed on line for public use.  If necessary, the Contractor shall drain the tank and repeat the disinfecting procedure at no additional cost to the Owner until approval for use is obtained.

B.	The tank bowl’s interior paint system shall be allowed to cure a minimum of 7 days, or longer, as recommended by the paint manufacturer according to ambient temperature, before the cleaning and disinfecting process is initiated.

C.	The Owner will furnish water for the initial disinfecting at no charge.  The Owner reserves the right to charge for water required for repeated attempts at disinfecting.

The contractor shall submit his proposed method of disinfecting to the Engineer for approval as part of shop drawing submittals.

D.	The Contractor shall be responsible for obtaining water sample bottles and the actual water samples and submitting the same to said State Authority.

3.08			WORKMANSHIP AND CLEANUP

- The contractor shall keep the premises clean at all times and shall remove all rubbish

as often as directed by the Engineer.  All debris is to be removed from the grounds.

3.09		BASIS OF PAYMENT

- Measurement shall be made for each water storage facility with all work complete;

tank full, bacteriological accepted, and ready for use: including all material, labor, and equipment necessary to complete the work in accordance with the Contract Documents

END OF SPECIFICATION