SPECIFIER NOTE:

This specification is provided by Mid-Atlantic Coatings, Inc. as a service and is intended to be used as a guideline for preparing a project specific specification section.  Every heading may not be needed.  Delete headings not used and renumber remaining used headings to be numerically correct.

PART 1 - GENERAL

  - GENERAL REQUIREMENTS

A.	Work of this section as shown or specified shall be in accordance with the requirements of the Contract Documents.

1.2	WORK INCLUDED

A.	Work of this section includes all labor, materials, equipment and services necessary to complete epoxy flooring incorporating broadcast aggregate technique and integral base as selected on drawings and/or specified herein.

  - RELATED SECTIONS

- Section 03 30 00 – Concrete: To be water cured or cured suing sodium silicate curing compound.

- Division 15 – Floor Drains: Flange type.

1.4	REFERENCES

- Society for Protective Coatings (SSPC) Specifications and Standards.

1.	SSPC-PA-3:	“A Guide to Safety in Paint Application”.

2.	SSPC-SP-13:  “Surface Preparation of Concrete”.

B.	NACE (National Association of Corrosion Engineers)

1.	NACE Publication 6D-173, “A Manual for Painter Safety”.

2.	NACE Publication 6G-164, “Surface Preparation Abrasives for Industrial Maintenance Painting”.

C.	ASTM (American Society for Testing and Materials)

1.	ASTM D4541 - L.R. “Standard Method for Pull-Off Strength of Coatings using Portable Adhesion Testers”.

2.	ASTM E337 - L.R. “Standard Practice Test Method for Measuring Humidity with a Psychrometer”.

3.	ASTM D4263-83 (1999), “Standard Test Method for Indicating Moisture in Concrete by the Plastic Sheet Method”.

4.	ASTM F1869-98, “Standard Test Method for Measuring Moisture Vapor Emission Rate of Concrete Subfloor Using Anhydrous Calcium Chloride”.

5.	ASTM D4414-95, “Standard Practice for Measurement of Wet Film Thickness by Notched Gages”.

6.	ICRI Guide No. 03732, “Selecting and Specifying Concrete Surface Preparation for Sealers, Coatings and Polymer Overlays,” International Concrete Repair Institute, Sterling, VA.

7.	ASTM 4262, “Standard Test Method for Measuring Surface pH of Acid Etched Concrete.”

8.	ASTM D 522, Flexibility

9.	ASTM D 579, Compressive Strength

10.	ASTM D 580, Flexural Strength And Modulus Of Elasticity

11.	ASTM D 790, Flexural Strength And Modulus Of Elasticity

13.	ASTM D 2047, Coefficient Of Friction

14.	ASTM D 2240, Hardness (Shore D Dorometer)

15.	ASTM D 2794, Impact

16.	ASTM D 3359, Adhesion

17.	ASTM D 3363, Hardness

18.	ASTM D 4060, Abrasion

19.	ASTM D4259, “Standard Practice for Abrading Concrete

D. 	USGBC LEED version 2.2

E.	Green Seal GS-03, GS-11

1.5 	SUBMITTALS

A.	General: Submit the following in accordance with Conditions of Contract and Division I Specification

Sections.

B.	Product Data: Submit manufacturer’s technical data, application instructions, performance criteria and

general recommendations for decorative epoxy flooring specified herein.

- Samples for initial selection purposes in form of manufacturer’s color charts showing range of standard

colors available.

1.	Submit 2-1/2” x 4” samples in color and quartz aggregate combination as selected.

- Material certificates signed by manufacturer certifying that the decorative quartz epoxy flooring submitted complies with the requirements specified herein.

- Maintenance Instructions: Submit manufacturer’s written instructions for recommended maintenance practices.

- LEED Submittals:  For Credit EQ 4.2, manufacturers' product data for coatings, including printed statement of VOC content and chemical components.

1.6 	QUALITY ASSURANCE

A.	Installer Qualifications: Engage an experienced installer or applicator that has specialized in installing resinous flooring types similar to that required for this Project and who is acceptable to manufacturer of primary materials.

B.	Single Source Responsibility: Obtain epoxy component of flooring materials, including primers, resins, hardening agents, and finish or sealing coats, from a single manufacturer. Obtain 30/50 washed silica sand aggregate from primary manufacturer of that product.

1.7 	DELIVERY STORAGE AND HANDLING

A.	Deliver materials in original packages and containers with seals unbroken and bearing manufacturer’s labels containing brand name and directions for storage and mixing with other components.

B.	Store materials to comply with manufacturer’s directions to prevent deterioration from moisture, heat, cold, direct sunlight, or other detrimental effects.

1.8 	PROJECT CONDITIONS

A.	Environmental Conditions: Comply with epoxy resin composition flooring manufacturer’s directions for maintenance of ambient and substrate temperature, moisture, humidity, ventilation, and other conditions required to execute and protect work.

- Lighting: Permanent lighting will be in place and working before installing decorative quartz epoxy flooring.

PART 2 - PRODUCTS

  - MATERIALS

A.	The laminate epoxy flooring shall be the Strata-Shield system as manufactured by Tnemec Company, Baltimore, MD and Kansas City, MO. Tel: 410-234-3600

B.	Equivalent materials of other manufacturers may be substituted only by approval of the Architect.

1.	Requests for substitution shall include manufacturer’s literature for each product giving the name,

generic type, descriptive information, solids by volume, test data and requirements, recommended

film thicknesses an a list of five projects where each product has been used and rendered satisfactory

service.

2.	No request for substitution shall be considered that would decrease film thickness or offer a change in the generic type of coating, performance criteria stated  herein or flooring specified.

3.	Substitutions shall be made 10 days prior to the bid date

C.	Bidders desiring to use coatings and floorings, other than those specified, shall submit those with

their proposal based on the specified materials, and indicate the sum which will be added to or

deducted from the base bid should alternate materials be accepted.

D.	Products for each specified function and system shall be of a single manufacturer.

  - PROPERTIES

A.	Colors: As indicated, or if not otherwise indicated, as selected by Architect from manufacturer’s standard color combinations.

B.	Broadcast, Grout and Seal coats Physical Properties: Series 237/238 Power Tread. Provide independent test data that meets or exceeds the listed minimum physical property requirements listed below. Test data shall be according to the referenced standard test method in parentheses.

1.	Compressive Strength (ASTM C 579)10,840 psi

2.	Hardness (ASTM D 2240) Durometer Rating 86

3.	Adhesion (ASTM D 4541) 400 psi (100% Concrete Failure)

4.	Water Absorption (ASTM C 413) 0.04% Water Absorption

5.	Abrasion Resistance (ASTM 4060) 91 mg loss

6.	Tensile Strength (ASTM D 638) 4983 psi (34.36MPa) Tensile Strength

7.	Tensile Strength (ASTM C 307) 2,125 psi (14.6 MPa) Tensile Strength

8.	Flexural Strength (ASTM D 790) 2,867 psi (19.768 MPa) Flexural Strength

9.	Modulus of Elasticity (ASTM D 790) 127,876 psi (881.67 MPa) Flexural Modulus

10.	Flexural Strength and Modulus of Elasticity (ASTM C 580, Method A)	4,300 psi (29.65 MPa)

Flexural Strength

11.	Impact (ASTM D 635) 240 inch pounds (27 J) average, direct impact

12.	Thermal Expansion (ASTM C 531) 1.145E-05 Linear coefficient of thermal expansion

13.	Shrinkage (ASTM C 531) 0.0017% Linear Shrinkage

C.	Finish Coat Physical Properties: Series 297 Enviro-Glaze. Provide independent test data that meets or exceeds the listed minimum physical property requirements listed below. Test data shall be according to the referenced standard test method in parentheses.

1.	Compressive Strength (ASTM C 579) 10,840 psi

2.	Hardness (ASTM D 2240) Durometer Rating 86

3.	Adhesion (ASTM D 4541 Method E, Type V) 400 psi (100% Concrete Failure)

Abrasion (ASTM D 4541 Method B, Type II) 390 psi (100% Concrete Failure)

4.	Water Vapor Transmission (ASTM C 413) 37 g/m2 per 24 hrs, 2.7 perms

5.	Abrasion Resistance (ASTM 4060) 30.7 mg loss

Abrasion Resistance (ASTM D 968) 48 litres per mil falling sand abrasion resistance

6.	Steam Resistance (2500 F Steam at 15-17 psi) Slight gloss loss after 4 hours continuous

exposure.

7.	Scrubbability (ASTM D 4213, 1000 cycles) 80 mg loss

8.	Stain Resistance (TTM-071 Covered Spot Test)No effect after 24 hours exposure to; Grape Jam,

Margarine, vinegar, lime juice, vegetable oil, crayon, dish soap, lipstick, toothpaste, 409 cleaner

& Clorox.

9.	Hardness (ASTM D 3363 Pencil) 5H (gouge)

10.	Flexibility (ASTM D 522, Method A, Conical)	27% elongation

11.	Coefficient of Friction (ASTM D 2047) 0.69static coefficient

12.	Chemical Resistance (TTM-59 Covered Spot Test) No blistering, cracking, checking, or

delamination of film. No more than slight softening & gloss loss after 24 hours exposure to the

following reagents; Acidulate 28, Enviro-Kleen 120, MB-10, Santi-Plex 128, LPH, Spor-Klenz,

and Vesphene II.

13.	Impact (ASTM D 635) 84 inch pounds direct impact

  - SUPPLEMENTAL MATERIALS

A.	Waterproofing Membrane: Shall be applied at elevated slabs and when directed by the architect or owner.

B.	Flexible Membrane Physical Properties:  Strata-Shield Series 206 Sub-Flex EP. Provide independent test data that meets or exceeds the listed minimum physical property requirements listed below. Test data shall be according to the referenced standard test method in parentheses.

1.	Hardness (ASTM D 2240) Type A Durometer Hardness of 98

2.	Adhesion (ASTM D 4541) 400 psi (100% Concrete Failure)

3.	Abrasion Resistance (ASTM 4060) 73 mg loss

4.	Tensile Strength (ASTM D 2370) 1,944 psi (13.4 MPa) Tensile Strength

5.	Elongation (ASTM D 2370) 94.5% Elongation and 382,600 psi (2,637 MPa) Tensile modulus

of Elasticity

6.	Tear Strength (ASTM D 5601) Not less than 7.5 pounds-force (33N) tear strength

7.	Impact (ASTM D 635) 160 inch pounds (18.08 J) average, direct impact

PART 3 - EXECUTION

3.1  	INSPECTION

- A.	Examine the areas and conditions where decorative quartz epoxy flooring is to be installed and notify the Architect of conditions detrimental to the proper and timely completion of the work. Do not proceed with the work until satisfactory conditions have been corrected by the Contractor in a manner acceptable to the Architect.

  - PREPARATION

A.	Substrate: Perform preparation and cleaning procedures according to the flooring manufacturer’s instructions for particular substrate condition involved, and as specified.

B.	Concrete Surfaces: Shot-blast or mechanically abrade to remove laitance, curing compounds, sealers and other contaminants and to provide surface profile.  (Reference ASTM D4259, ICRI CSP 5-7). Remove grease, oil, and other penetrating contaminates. Repair damaged, cracked and deteriorated concrete to an acceptable condition. Use an acceptable patching material recommended by the flooring manufacturer.

C.	Materials: Mix epoxy resin components when required, and prepare materials according to flooring system manufacturer’s instructions.

  - APPLICATION

A.	Moisture Content: Allow new concrete to cure for 28 days.  Verify dryness by testing for moisture with a “plastic film tape-down test”.  (Reference ASTM D4263).Should moisture be detected, perform “Standard Test Method for Measuring Moisture Vapor Emission Rate of Concrete Sub-floor Using Anhydrous Calcium Chloride.” (Reference ASTM F 1869). The moisture content shall not exceed three pounds per 1,000 sq ft in a 24 hour period. Contact Tnemec for additional information.

B.	General: Apply each component of resinous epoxy system according to manufacturer’s directions to produce a uniform monolithic flooring surface of thickness indicated.

C.	Primer Coat: Series 237/238-clear Power Tread applied at 6.0 to 8.0 mils or 200 to 267 sq ft per gallon.

D.	Membrane Coat: Series 206 Sub-Flex membrane shall be applied at 30.0 to 40.0 mils or 40 to 53 sq ft per gallon.

E.	Finish Coat: Apply Series 297 Enviro-Glaze at 2.0 to 3.0 mils DFT or 305 to 457 sq ft per gallon.

1.	Finished floor shall be 46 mils (with membrane) thickness.

E.	Cove Base: Apply cove base mixture of Series 237/238 (80-90 sq ft/gal) and 50/60 mesh washed silica sand to wall surfaces at locations shown to form cove base height of 4 inches unless otherwise indicated. Lay fiber-glass mesh tape into wet mixture at floor and wall transitions and joints. Follow manufacturer’s printed instructions and details including taping, mixing, priming, troweling, sanding, and top-coating

  - CLEANUP

A.	Remove waste materials, rubbish, and debris and dispose of them at the owner’s direction.  Leave work areas in a clean and tidy condition.

  - PROTECTION

A.	Protect the completed work from water, airborne particles or other surface contaminants until cured for a minimum of 24 hours after application.

B.	Protect from traffic, physical abuse, immersion and chemical exposure until the complete system has thoroughly cured for 24 hours at 75 degrees F.  For different temperatures, consult the manufacturer’s representative about curing times.

  - CURING PROTECTION AND CLEANING

- A.	Cured epoxy & polyurethane flooring materials according to manufacturer’s directions, taking care to prevent contamination during application stages and before completing curing process. The application area shall be closed down for a minimum of 24 hours.

END OF SECTION 09 67 23

RESINOUS EPOXY FLOORING